Legionella Written Scheme

Robinson House

February 2025

| Version | Author | Date | Comments/amendments |
| --- | --- | --- | --- |
| 1.0 | E Jorgenson | 22/07/2020 | N/A |
| 2.0 | E Jorgenson | 08/12/2020 | Updated after final risk assessment received, updated sections 7-13 |
| 3.0 | E Jorgenson | 18/03/2021 | Annual risk assessment review. |
| 4.0 | E Jorgenson | 21/10/2022 | Updated for risk assessment review and change in management structure |
| 5.0 | A Graham | 01/06/2023 | Update after new Risk Assessment carried out |
| 6.0 | A Graham | 16/04/2024 | Update due to new risk assessment contractor |
| 7.0 | A Graham | 17/02/2025 | Updated after new Risk assessment carried out |

Contents page

| Section number | Title | Page number |
| --- | --- | --- |
| 1 | Purpose | 3 |
| 2 | Scope | 3 |
| 3 | Risk Assessment | 3 |
| 4 | Management Structure | 4 |
| 5 | Asset Register | 6 |
| 6 | Scheme of Control | 8 |
| 7 | Record Keeping | 10 |
| 8 | Microbiological testing | 10 |
| 9 | Remedial Actions | 10 |
| 10 | Incident Plan | 11 |
| 11 | Actions in response to partial of full system shut down | 12 |
| 12 | Forms/Templates | 12 |
| 13 | Associated Documents | 13 |

- Purpose

The purpose of this document is to detail the site-specific written scheme for Robinson House

- Scope

This written scheme covers the domestic water system only within the property. There is no risk linked with any close systems in the property and therefore this has not been included in the scope.

- Risk Assessment

# All risk assessments for believe housing are completed by a Legionella Control Association registered company who have been selected through a full and proper procurement exercise.

# This risk assessment was carried out on the 13th January 2025. The site will be audited on an annual basis to assess the validity of the assessment and when it is considered no longer valid a new risk assessment will be arranged. The assessment may be considered invalid when;

- There are changes to the water system or its use;

- Changes to the use of the building in which the water system is installed

- The availability of checks indicating that control measures are no longer effective

- Changes in key personnel

- A case of legionnaires disease/legionellosis associated with the system.

# Following the risk assessment, an action plan has been formulated and details of this can be found located in on the following file path

Believe Housing 3ROBI1_Ext_Com_B27 ROBINSON HOUSE 1 27 Risk Assessment UKAS Accredited 1124389 Version 2.pdf

1124389 3ROBI1_Ext_Com_B27 ROBINSON HOUSE 1 27 Version 2 Schematic 130125.pdf

# This shows all the recommendations made in the risk assessment and the actions that believe housing are taking.

4. Management Structure

The management structure for the organisation is as follows.

| Statutory Duty Holder – Alan Smith |  |
| --- | --- |
| Position | Chief Executive |
| Address | believe housing, Coast House, Spectrum 4, Spectrum Business Park, Seaham |
| Postcode | SR7 7TT |
| Nominated Responsible Person – Emma Jorgenson |  |
| Position | Compliance Manager- Emma Jorgenson |
| Address | believe housing, Coast House, Spectrum 4, Spectrum Business Park, Seaham |
| Postcode | SR7 7TT |
| e mail | Emma.jorgenson@believehousing.co.uk |
| Training | City and Guilds Qualificatons “management of legionella bacteria in hot and cold water systems” and “hazard identification and risk assessment of water systems within buildings” and regular attendance of the north east councils legionella focus group (NECLFG). |
| Nominated Responsible Person (Deputy) – Andrew Graham |  |
| Position | Compliance Officer (Water) |
| Address | believe housing, Coast House, Spectrum 4, Spectrum Business Park, Seaham |
| Postcode | SR7 7TT |
| Phone | 07901510712 |
| e-mail | Andrew.graham@believehousing.co.uk |
| Training | City and Guilds Qualificatons “management of legionella bacteria in hot and cold water systems” and “hazard identification and risk assessment of water systems within buildings” and regular attendance of the north east councils legionella focus group (NECLFG). |
| Facilities Officer (Community Amenities, commpliance support) – Ines Carr |  |
| Address | believe housing, Coast House, Spectrum 4, Spectrum Business Park, Seaham SR7 7TT |
| Position | Facilities officer |
| Phone | 07769672356 |
| e-mail | Ines.Carr@believehousing.co.uk |
| Training | Believe housing online training |
| Risk Assessment Contractor – SMS Environmental |  |
| Address | Strathclyde Business Park, Suite1/2 Avondale House, Bellshill ML4 3NJ |
| Postcode | ML4 3NJ |
| Contact | Sharon David |
| Phone | 07521390672 |
| e-mail | s.david@sms-environmental.co.uk |

| Water Monitoring Contractor – HSL Compliance Ltd |  |
| --- | --- |
| Address | Tanfield Lea Business Centre, Tanfield Lea, Stanley DH9 9DB |
| Postcode | DH9 9DB |
| Contact | David Armstrong & Phil Lynas |
| Phone | 078233499745 & 07909706236 |
| e-mail | David.Armstrong@HSLcompliance.com & phil.lynas@HSLcompliance.com |
| Little used flushing - Contego |  |
| Address | Unit 4 , Maple Way, Aycliffe Business Park, Newton Aycliffe, County Durham, |
| Postcode | DL5 6BF |
| Phone | 07966473063 |
| e-mail | Martin.Ferguson@contegofacilities.com |

Full details regarding the responsibilities of the Duty Holder, Responsible Person and Deputy Responsible Person can be found in the legionella policy.

Full details of the responsibilities of the contractors employed by believe housing, to complete the legionella programs can be found detailed in the specification of the tender and water hygiene procedure.

- Asset Register

|  | Asset Number | Location (detail any specific access requirements) | Serving |
| --- | --- | --- | --- |
| Cold Water Storage Tanks |  | None |  |
| Water Heaters | CAL01 | Boiler Room | HWS Left (Linked to CAL2) |
|  | CAL02 | Boiler Room | HWS Right (Decommissioned and drained down) |
| Showers | SHR1 | Shower Room Next To Room 9 | 1 x SHR (Electric) |
|  | SHR2 | Flat 8 | 1 x SHR |
|  | SHR3 | Flat 20 | 1 x SHR (Electric) |
|  | SHR4 | First Floor Shower Room | 1 x SHR (Electric) |
|  | SHR5 | Flat 3 | 1 x SHR |
|  | SHR6 | Flat 18 | 1 x SHR |
|  | SHR7 | Flat 6 | 1 x SHR |
|  | SHR8 | Flat 11 | 1 x SHR |
|  | SHR9 | Flat 13 | 1 x SHR |
|  | SHR10 | Flat 14 | 1 x SHR |
|  | SHR11 | Flat 19 | 1 x SHR (hose and head removed from mixer tap no longer on maintenance regime) |
|  | SHR12 | Flat 25 | 1 x SHR |
|  | SHR 13 | Bungalow no 1 | 1 x SHR (Electric) |
|  | SHR 14 | Flat 21 | 1 x SHR (Customers own temp shower hose connection, added to quarterly cleaning plan) |
|  | SHR 15 | Flat 24 | 1 x SHR (Customers own temp shower hose connection, added to quarterly cleaning plan) |
| TMV’s | TMV1 | Kitchen | SINK |
|  | TMV2 | Ladies WC | WHB |
|  | TMV3 | Accessible WC | WHB |
|  | TMV4 | Gents WC | WHB |
|  | TMV5 | Flat 9 | WHB and BTH |
|  | TMV6 | Flat 10 | WHB and BTH |
|  | TMV7 | Flat 11 | WHB |
|  | TMV8 | Flat 11 | SHR |
|  | TMV19 | Flat 12 | WHB and BTH |
|  | TMV10 | Flat 13 | WHB and BTH |
|  | TMV11 | Flat 13 | SHR |
|  | TMV12 | Flat 14 | WHB |
|  | TMV13 | Flat 14 | SHR |
|  | TMV14 | Flat 2 | WHB and BTH |
|  | TMV15 | Flat 3 | WHB |
|  | TMV16 | Flat 3 | SHR |
|  | TMV17 | Flat 4 | WHB and BTH |
|  | TMV18 | Flat 5 | WHB and BTH |
|  | TMV19 | Flat 6 | SHR |
|  | TMV20 | Flat 6 | WHB |
|  | TMV21 | Flat 7 | WHB and BTH |
|  | TMV22 | Flat 8 | WHB and BTH |
|  | TMV23 | Flat 8 | SHR |
|  | TMV24 | Flat 20 | WHB and BTH |
|  | TMV25 | Flat 21 | WHB and BTH |
|  | TMV26 | Flat 15 | WHB and BTH |
|  | TMV27 | Flat 16 | WHB and BTH |
|  | TMV28 | Flat 17 | WHB and BTH |
|  | TMV29 | Flat 18 | WHB and BTH |
|  | TMV30 | Flat 18 | SHR |
|  | TMV31 | Flat 19 | WHB and BTH |
|  | TMV32 | Flat 22 | WHB and BTH |

|  | TMV33 | Flat 23 | WHB and BTH |
| --- | --- | --- | --- |
|  | TMV34 | Flat 24 | WHB and BTH |
|  | TMV35 | Flat 25 | WHB and BTH |
|  | TMV36 | Flat 25 | SHR |
|  | TMV 37 | Flat 25 | TMV Supplying shower (to be removed) |
|  | TMV38 | Flat 26 | WHB and BTH |
|  | TMV39 | Flat 27 | WHB and BTH |
| Other Systems | PV1 | Boiler House | CAL01 |

- Scheme of Control

  - Site description

Robinson House is a purpose-built Housing Plus Unit consisting of a bungalow which used to be the old warden’s home (number 1) and 26 self-contained flats (numbered 2-27). The water system comprises of one main fed calorifier (secondary calorifier decommissioned) located in the boiler house which feeds hot water to all flats, communal areas and bungalow in the property. All the cold water in the property is fed by mains supply.

  - Building use and access

The individuals living at the property all over 55 years old, with various believe housing representatives, contractors and friends and family visiting daily. Therefore, the population on this site will be considered as high risk in terms of legionella control.

Access to the communal areas of this property can be sought at any time. The main doors are on fob access, and these are available from the key safe at the property (code 1089). Where access to the tenants’ flats is required, contractors must liaise with the customers before any attempts at access are made.

  - Monitoring program

The risk assessment has shown that there is a reasonably foreseeable risk of legionella contamination in this building. Therefore, a scheme of control has been formulated and implemented at this site. The current program in place on site is a physical treatment program using temperature rather than biocides as a form of control. The specific program for this site is detailed as follows.

Weekly tasks

Currently it is not possible to confirm that there is constant water use in the communal areas of the building. Therefore, all communal outlets are flushed for five minutes weekly by the cleaning company Contego, and this action is recorded in the premises file in the site office.

This includes any Void properties which are identified.

Monthly tasks

HSL will visit the site once every month and monitor hot and cold-water temperatures.

Remote monitoring technology has been installed in the following locations in the property.

| Location | Floor | Item | Water Source |
| --- | --- | --- | --- |
| Community Kitchen | Ground Floor | Sink | WH1 |
| Flat 11 Kitchen | Ground Floor | Sink | WH1 |
| Flat 19 Kitchen | 1st Floor | Sink | WH1 |
| Flat 24 Kitchen | 1st Floor | Sink | WH1 |
| Flat 6 Kitchen | Ground Floor | Sink | WH1 |
| Guest Room Bathroom | 1st Floor | Bath | WH1 |

Remote monitoring outputs are collated into a report and sent to the Compliance team weekly to monitor and take any actions necessary.

Hot water temperatures will be taken from the flow and return of the heater located in the Boiler House.

Hot water temperatures will be taken from sentinels located in

| Location | Floor | Item | Water Source |
| --- | --- | --- | --- |
| Bungalow (No1) | Ground Floor | Sink (Furthest) | WH1 |
| Flat 6 | Ground Floor | Sink | WH1 |
| Communal Kitchen | Ground Floor | Sink | WH1 |
| Guest Room | First Floor | Bath (Nearest) | WH1 |
| Laundry | Ground Floor | Sink | WH1 |

Cold water temperatures will be taken from sentinel outlets located in

| Location | Floor | Item | Water Source |
| --- | --- | --- | --- |
| Bungalow (No1) | Ground Floor | Sink (Nearest) | MWS01 |
| Flat 6 | Ground Floor | Sink | MWS01 |
| Guest Room | First Floor | Sink (Furthest) | MWS01 |
| Laundry | Ground Floor | Sink | MWS01 |
| Boiler House Bib Tap | Ground Floor | Sink | MWS01 |

The temperature from every individual flat and communal outlet will be taken at least once annually. If an outlet is controlled by a TMV the temperature of the water entering the valve will be recorded.

All hot water from water heaters must be stored at above 60°C and supplied to hot outlets or thermostatic mixing valves at above 50°C within 1 minute. All cold water must be supplied to cold outlets or thermostatic mixing valves at below 20°C within 2 minutes.

Quarterly

The 15 showers located in the communal area and flats will be cleaned and disinfected quarterly in line with the method statements that HSL have submitted and in accordance with the ACoP L8 and HSG274 pt2.

The drain valve on the heaters located in the Boiler House will be opened on quarterly basis to purge all accumulated sludge from the vessel. If the drain water shows a high accumulation of dirt in the vessel a clean and disinfection will be carried out in line with the method statements that HSL has submitted and in accordance with the ACoP L8 (2014), and HSG 274 pt2.

The expansion vessel in the boiler house will be flushed through on a quarterly basis.

Six-monthly

All 39 TMV’s on site will be subject to failsafe testing on six monthly basis in accordance with the method statements submitted by HSL. If the valve does not pass the failsafe test it will be serviced fully or replaced.

Annually

All 39 TMV’s on site will be subject to a full service and failsafe testing on an annual basis in accordance with the method statements submitted by HSL. If the valve does not pass the failsafe test after being fully serviced, it will be replaced.

- Record Keeping

All records of site visits and little used flushing are kept in the site premises file with the risk assessment and this written scheme.

All other monitoring records are held on the web-based portal Socius which can be accessed by using the following log in detail.

Username: BelieveHousing@socius.com

Password: Thursday16

All records for legionella control will be kept for a minimum of 5 years as per the retention schedule detailed in the Approved Code of Practice L8.

- Microbiological testing

Due to the age and potential vulnerability of the occupants microbiological testing is completed monthly at all sentinel’s outlets and any other outlets identified as a cause for concern (e.g. little used, poor temperatures, poor flow etc). All samples taken monthly will be pre flush. If these samples results show levels above 100cfu/L or the correct temperatures are no being achieved (as detailed in section 5.3) the sample frequency will be immediately increased to weekly whilst the underlying issue is resolved. Following the resolution of the situation sampling frequency will be slowly reduced to monthly again.

All sampling will be completed in accordance with BS7592 “sampling for legionella organisms in water and related materials”. All samples will be set for analysis at a UKAS accredited laboratory with current ISO standard methods of detection and enumeration of legionella included in the scope of the accreditations. The laboratories used also take part in external QA proficiency schemes to provide extra assurance.

- Remedial Actions

On a regular basis, the Compliance Officer (Water), will check monitoring results on the web-based portal via exception report. All non-compliant results will subject to a desk top investigation to ascertain the extent and consistency of the issue. Where temperatures are consistently unable to achieve the required standards, or the monitoring raises other potential issues the Compliance Officer will raise relevant orders with Internal Repairs or external partners dependant of the works required. The Compliance Officer will advise on time scales for action depending on the risk the issue poses, which will be added to the ticket raised on QL. Where necessary legionella sampling may be requested on a weekly basis until the issue is resolved (see section 8).

Where issues with stagnation or lack of flushing are highlighted, due to a change of building use, the Contego will be advised so the little used flushing program can be extended or started to ensure the water turn over in the building is adequate.

- Incident Plan

Where contamination is identified in water systems the following action will be taken at the following thresholds.

| Legionella bacteria (cfu/l) | believe housing’s actions |
| --- | --- |
| up to 100 | In the sheltered housing schemes only; The primary concern is protecting susceptible residents and therefore if any legionella is detected an investigation will be carried out and the system resampled |
| >100 and up to 1000 | Either; - If the minority of samples are positive, the system will be resampled. If similar results are detected again, the control measures and risk assessment will be reviewed, and any remedial works identified and completed or; - If the majority of the samples taken are positive, the systems may be colonised at a low level. The control measures and risk assessment will be reviewed, and any remedial works identified and completed. A clean and disinfection of the system will be considered however the requirement for this will be decided on a case by case basis, considering all relevant factors. In both cases the system will be continually resamples until assurance is given that the system is back under control. |
| >1000 | The control measures and risk assessment will be reviewed, and any remedial works identified and completed. A clean and disinfection of the system will also be considered. The system will be continually resampled until assurance is given that the system is back under control. |

Where the thresholds above are met the Compliance Team will coordinate the organisations response to the incident. Where input is required from other areas of the organisation groups will be set up to coordinate the response, this may include but not be limited to the Compliance Manager, Assistant Director for Strategic Assets, Major Works Manager, Repairs and Maintenance Manager (Repairs), Facilities Coordinator, Health and Safety Officer, Neighbourhoods Team Leader and any third party contractors involved in the maintenance of the water system in the affected building.  An actions log will be started to document believe housings response to the contamination. This will be shared with the Compliance Manager and all other relevant parties as necessary.

Any incidents of contamination will be reported in the weekly compliance meeting and documented accordingly.

During this time the system will be sampled weekly. Further control measures may be introduced, such as point of use filtration and chemical dosing, to ensure the safety of any users or occupants. In some cases, buildings may have to be temporarily closed for works to be completed.

When works are complete the Compliance Team will continue to sample the system, reducing the frequency gradually until it is assured that control has been regained.

- Actions in response to partial of full system shut down

11.1 Temporary lack of use

Where the water usage in this property is temporarily reduced little used flushing will be expanded to include those areas which are no longer used. This flushing will be conducted weekly by Contego and a record of this will be made and placed in the legionella section of the premise’s logbook.

Where flats become void, these will be accessed, and flushed weekly by Contego, at the same time as the communal areas in the property. Where believe become aware that flats are still tenanted however are unoccupied, the Compliance Team will attempt to contact the tenant. Firstly, the tenant or tenant’s representative will be asked to attend the property weekly to flush all outlets. If they are not able to or it becomes apparent, they are not, believe will offer to complete this on their behalf as part of the property’s weekly checks. Where tenants are not willing to cooperate, this will be escalated to Neighbourhoods and Safer Neighbourhoods for assistance.

Where the entire property is out of use, the water system will be kept live and managed using hygiene flushing a least once per week at all outlets for a minimum of five minutes.

11.2 Recommissioning

Where hygiene flushing can’t be completed, or the water system has had to be drained the system will be fully recommissioned. Where the property has been drained down the system will be refilled, and then a cleansing flush completed before a clean and disinfection is carried out in accordance with method statements that HSL have submitted and in accordance with the ACoP L8 (2014), and HSG 274 pt2. Four days after the clean and disinfection is completed samples will be taken from the properties sentinel outlets to tested for coliforms, E. coli, 37 and 22C TVC’s and Legionella. Hygiene flushing will be undertaken weekly until the results are received. If Coliforms, E. coli, or elevated TVC’s are detected the sampling point will be cleaned, flushed and retested. If Legionella bacteria is detected the steps taken in section 10 of this written scheme will be taken and which may lead to the system being cleaned and disinfected again.

12 Forms/templates to be used

Little used flushing form

- Associated Documents

Water Hygiene Policy

Water Hygiene Procedure

Procurement Specification

COSHH records for chemicals used on site